## Cap.tech data sheet
LT Capacitors, 3 Phase, 50 Hz, 400/415/440/480/525 VAC
Sr No | DETAILS | DESCRIPTION | HEAVY DUTY | NORMAL DUTY | BOX TYPE
1 | Applicable Standards |  | IS-13340:2012 | IS-13340:2012 | IS-13340:2012
2 | Technical details | Rated Voltage | 400 / 415 / 440 / 480 / 525 VAC | 440 / 415 VAC | 400 / 415 / 440 / 480 / 525 VAC
|  | Frequency | 50 Hz / 60 Hz | 50 Hz / 60 Hz | 50 Hz / 60 Hz
|  | Losses (tan delta) | 0.0025 MAX. | 0.0025 MAX. | 0.0025 MAX.
|  | Peak inrush current | 200 TIMES | 150 TIMES | 200 TIMES
|  | Over voltage | 10% | 10% | 10%
|  | Over current | 10% | 10% | 10%
|  | Life expectancy | 100000 WORKING HRS. | 80000 WORKING HRS. | 100000 WORKING HRS.
|  | Capacitance tolerance | +5% | +5% | +5%
|  | Voltage Test Between terminals | 1.75 TIMES OF RATED VOLTAGE | 1.75 TIMES OF RATED VOLTAGE | 1.75 TIMES OF RATED VOLTAGE
|  | Voltage Test Between earth & terminals | 3 KVAC | 3 KVAC | 3 KVAC
|  | Discharge resistors | CFR | CFR | CFR
|  | Safety | PRESSURE INTERRUPT | PRESSURE INTERRUPT | PRESSURE INTERRUPT
|  | Terminal casing | DOUBLE HOUSING | DOUBLE HOUSING | DOUBLE HOUSING
|  | Casing | CYLINDRICAL ALLUMINIUM CAN / SQUARE TYPE | CYLINDRICAL ALLUMINIUM CAN / SQUARE TYPE | CRCA SQUARE BOX
|  | Number of Elements | 3 | 3 | 3 no's / 6 no's
|  | Dielectric | METALLISED POLYPROPELENE FILM | METALLISED POLYPROPELENE FILM | METALLISED POLYPROPELENE FILM
|  | Impregnation | EPOXY | EPOXY | EPOXY
|  | Ambient temperature | 50°C | 50°C | 50°C
|  | Temperature rise (°C) | 10°C | 10°C | 10°C
|  | Location | OUTDOOR / INDOOR | OUTDOOR / INDOOR | OUTDOOR / INDOOR
|  | Type | MPP-SH | MPP-SH | MPP-SH
|  | Insulation level | 3 KVAC | 3 KVAC | 3 KVAC
|  | Type of capacitor bank connection | DELTA | DELTA | DELTA
|  | Discharge device | RESISTORS | RESISTORS | RESISTORS
regards,
Mr.PRADIP.V.BHARGAWE
Director
SHRICAP ELECTRONICS
G-21,MIDC,SATPUR,NASHIK-422007

## Cap.tech data sheet (2)
SPECIFICATIONS FOR LT SHUNT CAPACITORS (3 Phase, 50 Hz,)
Sr No | Detail | Descriptions | Vendor Confirmation
1 | Applicable Standards | Shunt capacitors for power system | IS-13340
IEC-60831-1
2 | Technical details | Rated Voltage | UPTO 600 VAC
|  | Frequency | 50Hz
|  | Losses(Dielectrical) (Watt/KVAr) | Max. 0.5 Watt/Per Kvar
|  | Peak inrush current | AS PER IS/IEC
|  | Over voltage | 10%
|  | Over current | 10%
|  | Mean life expectancy | 100000 WORKING HRS.
|  | Capacitance tolerance | +10% / -5%
Voltage test
|  | Between terminals | 1.75 TIMES
|  | Between Body & terminals | 3 KVAC
|  | Safety | PRESSURE INTERPTURE
|  | Casing | AL. CAN/CRCA
|  | Dielectric | MPP FILM
|  | Impregnation | POLYURETHIN EPOXY
|  | Temperature Categery | 50°C
|  | Temperature rise (°C) | 10 °C ABOVE AMBIENT
|  | Type | MPP SH
|  | Insulation level | 3 KVAC
|  | Type of capacitor bank connection | DELTA
|  | Discharge device | RESISTORS
|  | Mounting for Aluminium Round Can | Bottom Stud
|  | Mounting for Box Type | Floor Mounting
|  | Outdoor/Indoor | As per Reuqirement

## Heavy Duty
Sr No | DETAILS | DESCRIPTION | HEAVY DUTY
1 | Applicable Standards |  | IS-13340:2012
2 | Technical details | Rated Voltage | 400 / 415 / 440 / 480 / 525 VAC
|  | Frequency | 50 Hz / 60 Hz
|  | Losses (tan delta) | 0.0025 MAX.
|  | Peak inrush current | 200 TIMES
|  | Over voltage | 10%
|  | Over current | 10%
|  | life expectancy | 100000 WORKING HRS.
|  | Capacitance tolerance | +5%
|  | Voltage Test Between terminals | 1.75 TIMES OF RATED VOLTAGE
|  | Voltage Test Between earth & terminals | 3 KVAC
|  | Discharge resistors | CFR
|  | Safety | PRESSURE INTERRUPT
|  | Terminal casing | DOUBLE HOUSING
|  | Casing | CYLINDRICAL ALLUMINIUM CAN / SQUARE TYPE
|  | Number of Elements | 3
|  | Dielectric | METALLISED POLYPROPELENE FILM
|  | Impregnation | EPOXY
|  | Ambient temperature | 50°C
|  | Temperature rise (°C) | 10 °C
|  | Location | OUTDOOR / INDOOR
|  | Type | MPP-SH
|  | Insulation level | 3 KVAC
|  | Type of capacitor bank connection | DELTA
|  | Discharge device | RESISTORS

## Normal Duty
Sr No | DETAILS | DESCRIPTION | NORMAL DUTY
1 | Applicable Standards |  | IS-13340:2012
2 | Technical details | Rated Voltage | 415 / 440 VAC
|  | Frequency | 50 Hz / 60 Hz
|  | Losses (tan delta) | 0.0025 MAX.
|  | Peak inrush current | 150 TIMES
|  | Over voltage | 10%
|  | Over current | 10%
|  | life expectancy | 80000 WORKING HRS.
|  | Capacitance tolerance | +5%
|  | Voltage Test Between terminals | 1.75 TIMES OF RATED VOLTAGE
|  | Voltage Test Between earth & terminals | 3 KVAC
|  | Discharge resistors | CFR
|  | Safety | PRESSURE INTERRUPT
|  | Terminal casing | DOUBLE HOUSING
|  | Casing | CYLINDRICAL ALLUMINIUM CAN / SQUARE TYPE
|  | Number of Elements | 3
|  | Dielectric | METALLISED POLYPROPELENE FILM
|  | Impregnation | EPOXY
|  | Ambient temperature | 50°C
|  | Temperature rise (°C) | 10 °C
|  | Location | OUTDOOR / INDOOR
|  | Type | MPP-SH
|  | Insulation level | 3 KVAC
|  | Type of capacitor bank connection | DELTA
|  | Discharge device | RESISTORS

## Box Type
Sr No | DETAILS | DESCRIPTION | BOX TYPE
1 | Applicable Standards |  | IS-13340:2012
2 | Technical details | Rated Voltage | 400 / 415 / 440 / 480 / 525 / 660 VAC
|  | Frequency | 50Hz
|  | Losses (tan delta) | 0.0025 MAX.
|  | Peak inrush current | 200 TIMES
|  | Over voltage | 10%
|  | Over current | 10%
|  | life expectancy | 100000 WORKING HRS.
|  | Capacitance tolerance | +5%
|  | Voltage Test Between terminals | 1.75 TIMES OF RATED VOLTAGE
|  | Voltage Test Between earth & terminals | 3 KVAC
|  | Discharge resistors | CFR
|  | Safety | PRESSURE INTERRUPT
|  | Terminal casing | DOUBLE HOUSING
|  | Casing | CRCA SQUARE BOX
|  | Number of Elements | 3 no's / 6 no's
|  | Dielectric | METALLISED POLYPROPELENE FILM
|  | Impregnation | EPOXY
|  | Ambient temperature | 50°C
|  | Temperature rise (°C) | 10 °C
|  | Location | OUTDOOR / INDOOR
|  | Type | MPP-SH
|  | Insulation level | 3 KVAC
|  | Type of capacitor bank connection | DELTA
|  | Discharge device | RESISTORS